# Built-in window louvre DucoGrille Classic F 20V

Manufactured by: DUCO Ventilation & Sun Control

DucoGrille Classic F 20V is a recessed window louvre manufactured from extruded aluminium profiles. Quick and easy assembly is possible because of the ‘Turn-Click’ system. Insect mesh is fitted as standard. The unique “V”-shaped blade ensures better water resistance and makes the louvre grille ‘penetration-proof’ and difficult to see through from the outside.

## Features:

- Blade height: 20 mm

- Louvre pitch: 20 mm

- Flange width: 24 mm

- Frame depth: 35 mm

- Section thickness: minimum 1.2 mm

- Visual free area: 95 %

- Physical free area: 34%

## Accessories (included):

- Insect-resistant stainless steel mesh 2.3 x 2.3 mm (standard) or vermin-resistant mesh (on request)

## Surface treatment:

- Anodisation: Qualanod-compliant, coating thickness 15-20µm, standard natural colour (colourless anodisation)

- Powder coating: Qualicoat Seaside type A compliant, minimum average coating thickness 60µm, standard RAL colours 70% gloss

Upon request: other finish coating thicknesses, anodising colours and paint gloss levels, textured paints and specific powder coating product codes

## Functional specifications:

### Flow rate standard version:

  - K-factor inlet: 41.62

  - K-factor outlet: 41.62

  - Ce coefficient: 0.155

  - Cdcoefficient: 0.155

### Flow rate version "+ options":

  - K-factor inlet: 45.04

  - K-factor outlet: 45.04

  - Ce coefficient: 0.149

  - Cdcoefficient: 0.149

### Water repellency standard version:

  - v = 0.0m/s: class A

  - v = 0.5m/s: class B

  - v = 1.0m/s: class C

  - v = 1,5m/s: class D

  - v = 2.0m/s: class D

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

### Water repellency version "+ options":

  - v = 0.0m/s: class A

  - v = 0.5m/s: class A

  - v = 1.0m/s: class B

  - v = 1.5m/s: class B

  - v = 2.0m/s: class C

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

## Complies with or tested in accordance with the following standards:

- Qualicoat Seaside type A (if painted finish)

- Qualanod (if anodised finish)

- EN 573 - EN AW-6063 T66 and EN AW-6060 T66: aluminium alloy & hardening

- EN 13030: water resistance and determination of Ce and Cd coefficients