# Built-in wall louvre DucoGrille Classic G 50/75Z

Manufactured by: DUCO Ventilation & Sun Control

DucoGrille Classic G 50/75Z is a recessed wall louvre manufactured from extruded aluminium sections. Quick and easy assembly is possible because of the ‘Turn-Click’ system. Insect mesh is fitted as standard. The unique “Z”-shaped louvre blade produces a stylish design.

## Features:

- Blade height: 76 mm

- Louvre pitch: 75 mm

- Frame rebate: 48 mm

- Installation depth: 62 mm

- Section thickness: minimum 1.5 mm

- Visual free area: 80 %

- Physical free area: 49 %

## Accessories (included):

- Insect-resistant stainless steel mesh 2.3 x 2.3 mm (standard) or vermin-resistant mesh (on request)

- Fixing lugs

## Surface treatment:

- Anodisation: Qualanod-compliant, coating thickness 15-20µm, standard natural colour (colourless anodisation)

- Powder coating: Qualicoat Seaside type A compliant, minimum average coating thickness 60µm, standard RAL colours 70% gloss

Upon request: other finish coating thicknesses, anodising colours and paint gloss levels, textured paints and specific powder coating product codes

## Functional specifications:

### Flow rate standard version:

  - K-factor inlet: 17.51

  - K-factor outlet: 12.94

  - Ce coefficient: 0.239

  - Cdcoefficient: 0.278

### Flow rate version "+ options":

  - K-factor inlet: 20.85

  - K-factor outlet: 12.06

  - Ce coefficient: 0.219

  - Cdcoefficient: 0.288

### Water repellency standard version:

  - v = 0.0m/s: class C

  - v = 0.5m/s: class C

  - v = 1.0m/s: class C

  - v = 1,5m/s: class D

  - v = 2.0m/s: class D

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

### Water repellency version "+ options":

  - v = 0.0m/s: class A

  - v = 0.5m/s: class B

  - v = 1.0m/s: class B

  - v = 1,5m/s: class C

  - v = 2.0m/s: class C

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

## Complies with or tested in accordance with the following standards:

- Qualicoat Seaside type A (if painted finish)

- Qualanod (if anodised finish)

- EN 573 - EN AW-6063 T66 and EN AW-6060 T66: aluminium alloy & hardening

- EN 13030: water resistance and determination of Ce and Cd coefficients