Recessed wall-mounted grille Duco Acoustic Panel 150

Manufactured by: DUCO Ventilation & Sun Control

Duco Acoustic Panel 150 is a sound-absorbing recessed mounted wall louvre, manufactured from extruded aluminium profiles. The louvre blades are set in an aluminium frame and have sound-absorbing, non-flammable mineral wool inside.

Features:

- Louvre shape: Acoustic 150

- Louvre pitch: 130 mm

- Frame rebate: 37 mm

- Installation depth: 157 mm

- Section thickness: minimum 1.5 mm

- Visual free area: 71 %

- Physical free area: 31 %

- Water gutter: no water gutter, standard bottom sill sloping outwards inclination 5°

- Fastening: to side, via holes provided in the side plates of the module (diameter 5.5mm, countersunk) . Fixing materials depending on customer structure (not supplied by DUCO).

Accessories:

- Optional with insect mesh 2.3 x 2.3 mm

- Optional with vermin-resistant mesh 6 x 6 mm

- Optional with vermin-resistant mesh 20 x 20 mm

Surface treatment:

- Powder coating: Qualicoat Seaside type A compliant, minimum average coating thickness 60µm, standard RAL colours 70% gloss

Upon request: other finish coating thicknesses and paint gloss levels, textured paints and specific powder coating product codes

Functional specifications:

### Flow rate standard version:

  - K-factor inlet: 15.87

  - K-factor outlet: 16.26

  - Ce coefficient: 0.251

  - Cdcoefficient: 0.248

### Flow rate version "+ options":

  - K-factor inlet: 17.95

  - K-factor outlet: 16.26

  - Ce coefficient: 0.236

  - Cdcoefficient: 0.248

### Water resistance standard version:

  - v = 0.0m/s: class C

  - v = 0.5m/s: class D

  - v = 1.0m/s: class D

  - v = 1,5m/s: class D

  - v = 2.0m/s: class D

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

### Water repellency version "+ options":

  - v = 0.0m/s: class B

  - v = 0.5m/s: class C

  - v = 1.0m/s: class D

  - v = 1,5m/s: class D

  - v = 2.0m/s: class D

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

- Attenuation value

  - Rw (C;Ctr) (in dB): 11 (-1;-2)

| Sound reduction index |  |
| --- | --- |
| Hz | dB |
| 125 | 4,8 |
| 250 | 4 |
| 500 | 7,4 |
| 1000 | 11,4 |
| 2000 | 12,4 |
| 4000 | 13 |
| Rw(C;Ctr) | 11 (-1;-2) |

Complies with or tested in accordance with the following standards:

- Qualicoat Seaside type A

- EN 573 - EN AW-6063 T66 and EN AW-6060 T66: aluminium alloy & hardening

- EN 13030: water resistance and determination of Ce and Cd coefficients

- EN ISO 10140: acoustic measurements (for acoustic products)