# Recessed wall-mounted grille Duco Acoustic Panel 300

Manufactured by: DUCO Ventilation & Sun Control

DucoGrille Acoustic Panel 300 is a sound-absorbing recessed mounted wall louvre, manufactured from extruded aluminium sections. The louvre blades are set in an aluminium frame and have sound-absorbing, non-flammable mineral wool inside.

## Features:

- Louvre shape: Acoustic 150

- Louvre pitch: 130 mm

- Frame rebate: 37 mm

- Installation depth: 300 mm

- Section thickness: minimum 1.5 mm

- Visual free area: 71 %

- Physical free area: 31 %

- Water gutter: no water gutter, standard bottom sill sloping outwards inclination 5°

- Fastening: to side, via holes provided in the side plates of the module (diameter 5.5mm, countersunk) . Fixing materials depending on customer structure (not supplied by DUCO).

## Accessories:

- Optional with insect mesh 2.3 x 2.3 mm

- Optional with vermin-resistant mesh 6 x 6 mm

- Optional with vermin-resistant mesh 20 x 20 mm

## Surface treatment:

- Powder coating: Qualicoat Seaside type A compliant, minimum average coating thickness 60µm, standard RAL colours 70% gloss

Upon request: other finish coating thicknesses and paint gloss levels, textured paints and specific powder coating product codes

## Functional specifications:

### Flow rate standard version:

  - K-factor inlet: 26.75

  - K-factor outlet: 27.41

  - Ce coefficient: 0.194

  - Cdcoefficient: 0.191

### Flow rate version "+ options":

  - K-factor inlet: 31.92

  - K-factor outlet: 27.41

  - Ce coefficient: 0.177

  - Cdcoefficient: 0.191

### Water resistance standard version:

  - v = 0.0m/s: class C

  - v = 0.5m/s: class D

  - v = 1.0m/s: class D

  - v = 1,5m/s: class D

  - v = 2.0m/s: class D

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

### Water repellency version "+ options":

  - v = 0.0m/s: class B

  - v = 0.5m/s: class C

  - v = 1.0m/s: class D

  - v = 1,5m/s: class D

  - v = 2.0m/s: class D

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

### Attenuation value

  - Rw (C;Ctr) (in dB): 17 (-1;-4)

| Sound reduction index |  |
| --- | --- |
| Hz | dB |
| 125 | 6,3 |
| 250 | 5,9 |
| 500 | 11,6 |
| 1000 | 20,1 |
| 2000 | 22,7 |
| 4000 | 21,5 |
| Rw(C;Ctr) | 17 (-1;-4) |

## Complies with or tested in accordance with the following standards:

- Qualicoat Seaside type A

- EN 573 - EN AW-6063 T66 and EN AW-6060 T66: aluminium alloy & hardening

- EN 13030: water resistance and determination of Ce and Cd coefficients

- EN ISO 10140: acoustic measurements (for acoustic products)