# Window louvre – DUCO Ventilation & Sun Control
DucoGrille Solid ISO F 30Z

## Description

DucoGrille Solid ISO F 30Z is an architectural window louvre made of aluminium extrusion profiles. The grille has good thermal insulation thanks to the well-thought-out combination of a thermally broken frame with an insulation panel. The louvre blades offer high ventilation capacity with relatively small louvre blades. The ‘stackable’ louvre blades form a single whole, making them extra strong. The louvre blades are available with small punching (P1) or large punching (P2). A round or rectangular duct can be connected to the back of the grille. The grille with small punching (P1) is also optionally available with burglar resistance class 2 according to standards NEN 5096 and ENV 1627.

## Version

- Shape of blade	30Z

- Punching		NP – not punched

P1 – height 21 mm x width 2,5 mm

P2 – height 21 mm x width 18 mm

- Pitch			37,5 mm

- Frame width		63 mm

- Glass thickness	24/28/32/36/40/44/48 mm

- Frame depth		88 mm (thermally broken)

- Mesh			Punching

P1 as insect mesh

P2 as rodent mesh

Stainless-steel mesh

2,3 x 2,3 mm as insect mesh

6 x 6 mm as rodent mesh

20 x 20 mm as bird mesh

- Duct connection	Round duct

maximum smallest dimension for width or height - (2x63)

Rectangular duct

Duct height: grille height - (2x63)

Duct width: grille width - (2x63)

- Burglar resistant	Optional with P1 ponsing

Class 2 (NEN 5096:2007 and ENV 1627:2011)

The following combinations are available in all glass thicknesses::

|  | P1 | P1 Incl mesh | P2 |
| --- | --- | --- | --- |
| Punching P1 | S | S | - |
| Punching P2 | - | - | S |
| Stainless-steel mesh 2,3 x 2,3 | - | S | O |
| Burglar resistant (class 2) | O | O | - |

S = standard		O = optional

## Material and surface treatment

- Aluminium		EN AW-6063 T66 (EN 573-3)

Profile thickness: min. 1,5 mm

- Insulation		Akotherm

- Finish

  - Natural anodised (15-20 μm) according to Qualanod

  - Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

## Technical specifications

### U-value

0,9 W/m2K

### Burglar resistant

Optional with P1 punching: Class 2 (NEN 5096:2007 and ENV 1627:2011)

### Free area

|  | P1 P1 incl mesh | P2 |
| --- | --- | --- |
| Visual free area (Per metre punching) | 60 % | 86 % |
| Physical free area | 34 % | 48 % |

### Airflow data

| EN 13030 | P1 | P1 Incl mesh | P2 |
| --- | --- | --- | --- |
| Ce | 0,243 | 0,233 | 0,258 |
| K-factor intake | 16,94 | 18,42 | 15,02 |
| Cd | 0,234 | 0,224 | 0,253 |
| K-factor exhaust | 18,26 | 19,93 | 15,62 |

### Water resistance

| EN 13030 | P1 | P1 Incl mesh | P2 |
| --- | --- | --- | --- |
| V = 0 m/s | B | C | C |
| V = 0,5 m/s | C | C | C |
| V = 1 m/s | C | C | C |
| V = 1,5 m/s | D | C | D |
| V = 2 m/s | D | D | D |
| V = 2,5 m/s | D | D | D |
| V = 3 m/s | D | D | D |
| V = 3,5 m/s | D | D | D |