# Wall louvre – DUCO Ventilation & Sun Control
DucoGrille Solid++ M 30Z

## Description

DucoGrille Solid++ M 30Z is a burglar resistant surface mounted wall louvre made of aluminium extrusion profiles with a reinforced frame profile. The louvre blades offer high ventilation capacity with relatively small louvre blades. The ‘stackable’ louvre blades form a single whole, making them extra strong. The grille achieves burglar resistance class 2 according to NEN 5096 and ENV 1627 standards.

## Version

- Shape of blade	30Z

- Punching		P1 – height 21 mm x width 2,5 mm

- Pitch			37,5 mm

- Frame width		56 mm

- Installation depth	42 mm

- Frame depth		42 mm

- Mesh			Punching

P1 as insect mesh

Stainless-steel mesh

2,3 x 2,3 mm as insect mesh

The following combinations are available:

|  | P1 | P1 Incl mesh |
| --- | --- | --- |
| Punching P1 | S | S |
| Stainless-steel mesh 2,3 x 2,3 | - | S |

S = standard

## Material and surface treatment

- Aluminium		EN AW-6063 T66 (EN 573-3)

Profile thickness: min. 1,5 mm

- Finish

  - Natural anodised (15-20 μm) according to Qualanod

  - Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

## Technical specifications

### Reaction to fire

AS-s1,d0 (EN 13501-1)

### Burglar resistance class

Class 2 (NEN 5096:2007 and ENV 1627:2011)

### Fall-through protection

Class XI (BS 6180)

### Free area

|  | P1 P1 incl mesh |
| --- | --- |
| Visual free area (Per metre punching) | 60 % |
| Physical free area | 34 % |

### Airflow data

| EN 13030 | P1 | P1 Incl mesh |
| --- | --- | --- |
| Ce | 0,243 | 0,233 |
| K-factor intake | 16,94 | 18,42 |
| Cd | 0,234 | 0,224 |
| K-factor exhaust | 18,26 | 19,93 |

### Water resistance

| EN 13030 | P1 | P1 Incl mesh |
| --- | --- | --- |
| V = 0 m/s | B | C |
| V = 0,5 m/s | C | C |
| V = 1 m/s | C | C |
| V = 1,5 m/s | D | C |
| V = 2 m/s | D | D |
| V = 2,5 m/s | D | D |
| V = 3 m/s | D | D |
| V = 3,5 m/s | D | D |