# Recessed mounted wall louvre
DUCO Ventilation & Sun Control
Duco Acoustic Panel 150

## Description

Duco Acoustic Panel 150 is a sound absorbing recessed mounted wall louvre, manufactured from aluminium extrusion profiles. The blades are placed in an aluminium frame and are fitted with sound absorbing, non-combustible mineral wool on the inside.

## Version

### Blade

- Shape of blade	Acoustic 150

- Pitch			130 mm

### Frame

- Frame width		25 mm

- Flange depth		37 mm

- Frame depth		157 mm

- Drainage		standard bottom of sill sloping downwards towards the outside

inclination 5°

### Fastening

- To the side, through holes provided in the side plates of the module (diameter 5.5 mm, countersunk).

- Fastening materials depend on the underlying structure (not supplied by DUCO).

### Accessories (+ options)

- Additional frame with insect mesh 2.3 x 2.3 mm.

- Additional frame with pest-proof mesh 6 x 6 mm.

- Additional frame with bird-proof mesh 20 x 20 mm.

## Material and surface treatment

### Blade

- Aluminium		EN AW-6063 T66

Profile thickness: min. 1.5 mm

- Finish

  - Natural anodised (15-20 μm) according to Qualanod

  - Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

### Side plates

- Aluminium		AlMg3

Plate thickness: 3 mm

- Finish

  - Natural anodised (15-20 μm) according to Qualanod

  - Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

## Technical specifications

### Reaction to fire

Damping material: A1 (EN 13501-1)

### Fire resistance

Damping material: non-combustible (NEN 6064)

### Free area

| Feature | Duco Acoustic Panel 150 |  |
| --- | --- | --- |
|  | STD | +OPT |
| Visual free area | 71 % | 71 % |
| Physical free area | 31 % | 31 % |

### Flow rates

| Feature | Duco Acoustic Panel 150 |  |
| --- | --- | --- |
|  | STD | +OPT |
| Ce | 0.304 | 0.280 |
| K-factor intake | 10.82 | 12.76 |
| Cd | 0.297 | 0.282 |
| K-factor exhaust | 11.34 | 12.57 |

### Water resistance

| Velocity v (m/s) | Duco Acoustic Panel 150 |  |
| --- | --- | --- |
|  | STD | +OPT |
| 0 | C | C |
| 0.5 | D | D |
| 1 | D | D |
| 1.5 | D | D |
| 2 | D | D |
| 2.5 | D | D |
| 3 | D | D |
| 3.5 | D | D |

### Attenuation value

| in dB | Duco Acoustic Panel 150 |
| --- | --- |
| Rw (C;Ctr) | 11 (-1;-2) |
| 125 Hz | 5.3 |
| 250 Hz | 6.0 |
| 500 Hz | 6.2 |
| 1000 Hz | 11.3 |
| 2000 Hz | 13.3 |
| 4000 Hz | 11.3 |

### Impact resistance*

| Class | Duco Acoustic Panel 150 |
| --- | --- |
| EN 13049 | 5 |
| NF P08-302 | Q4 |

* Depending on fastening and dimensions.

### Fall-through protection*

| Class | Duco Acoustic Panel 150 |
| --- | --- |
| B03-004 | C5b |
| NEN-EN 1991-1-1 | A/B/F/G |
| NF P01-013 | C5 |
| BS 6180 | XI |

* Depending on fastening and dimensions.

Please consult your regional dealer or the DUCO “Ventilation & Sun Control” project department for commercial and technical support (mounting instructions, parts lists, calculations …).