# Recessed mounted wall louvre DucoGrille Classic G 70V Vertical

Manufactured by: DUCO Ventilation & Sun Control

DucoGrille Classic G 70V Vertical is a recessed mounted wall louvre made of aluminium extrusion profiles. Quick and easy assembly is possible because of the ‘Turn-Click’ system. Insect mesh is fitted as standard. The unique “V”-shaped louvre blade produces a stylish design.

Due to the vertical mounting of the louvres, the grille scores even better in terms of water resistance and no see-through is possible.

## Features:

- Blade height: 71 mm

- Louvre pitch: 65 mm

- Frame width: 60 mm

- Frame rebate: 48 mm

- Installation depth: 89 mm

- Section thickness: minimum 1.5 mm

- Visual free area: 65 %

- Physical free area: 36%

## Accessories (included):

- Insect-resistant stainless steel mesh 2.3 x 2.3 mm (standard) or vermin-resistant mesh (on request)

- Fixing lugs

- With version "+options": water channel at the back of the frame

## Surface treatment:

- Anodisation: Qualanod-compliant, coating thickness 15-20µm, standard natural colour (colourless anodisation)

- Powder coating: Qualicoat Seaside type A compliant, minimum average coating thickness 60µm, standard RAL colours 70% gloss

Upon request: other finish coating thicknesses, anodising colours and paint gloss levels, textured paints and specific powder coating product codes

## Functional specifications:

### Flow rate standard version:

  - K-factor inlet: 73.05

  - K-factor outlet: 84.17

  - Ce coefficient: 0.117

  - Cdcoefficient: 0.109

### Flow rate version "+ options":

  - K-factor inlet: 81.16

  - K-factor outlet: 94.26

  - Ce coefficient: 0.111

  - Cdcoefficient: 0.103

### Water repellency standard version:

  - v = 0.0m/s: class A

  - v = 0.5m/s: class A

  - v = 1.0m/s: class A

  - v = 1,5m/s: class C

  - v = 2.0m/s: class C

  - v = 2.5m/s: class D

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

### Water repellency version "+ options":

  - v = 0.0m/s: class A

  - v = 0.5m/s: class A

  - v = 1.0m/s: class A

  - v = 1.5m/s: class A

  - v = 2.0m/s: class A

  - v = 2.5m/s: class C

  - v = 3.0m/s: class D

  - v = 3.5m/s: class D

## Complies with or tested in accordance with the following standards:

- Qualicoat Seaside type A (if painted finish)

- Qualanod (if anodised finish)

- EN 573 - EN AW-6063 T66 and EN AW-6060 T66: aluminium alloy & hardening

- EN 13030: water resistance and determination of Ce and Cd coefficients