Continuous louvre walls DucoWall Acoustic W 300

Manufactured by: DUCO Ventilation & Sun Control

DucoWall Acoustic 300 : In this version, two 150 louvre blades are placed one after the other, so that optimum sound absorption can be achieved. Nevertheless, the installation depth remains limited at 334 mm.

## Features:

- Louvre blades:

- Louvre height: 155.5 mm

- Louvre pitch: 150 mm

- Louvre blade depth : 30 mm

- Section thickness: minimum 1.5 mm

- Visual free area: 74 %

- Physical free area: 35%

- Support profiles:

Aluminium extrusions featuring a groove for securing the blade holders

Heavy-duty support profiles 21/50 Multi and 50/50: suitable for free overhang, attached to underlying structure by means of supplied L-profiles

- Blade holders: injection-moulded parts made of polyamide PA 6.6 glass-fibre reinforced

- Recess depth:

  - Support profile 50/50 or 21/50 Multi: 334 mm

## Surface treatment:

- Anodisation: Qualanod-compliant, coating thickness 15-20µm, standard natural colour (colourless anodisation)

- Powder coating: Qualicoat Seaside type A compliant, minimum average coating thickness 60µm, standard RAL colours 70% gloss

Upon request: other finish coating thicknesses, anodising colours and paint gloss levels, textured paints and specific powder coating product codes

## Functional specifications:

### Flow rate standard version:

  - K-factor inlet: 13.52

  - K-factor outlet: 13.52

  - Ce coefficient: 0.272

  - Cdcoefficient: 0.272

### Flow rate version "+ options":

  - K-factor inlet: 16.00

  - K-factor outlet: 16.00

  - Ce coefficient: 0.25

  - Cdcoefficient: 0.25

### Water resistance standard version:

  - v = 0.0m/s: class A

  - v = 0.5m/s: class B

  - v = 1.0m/s: class B

  - v = 1,5m/s: class C

  - v = 2.0m/s: class C

  - v = 2.5m/s: class D

  - v = 3.0m/s: class d

  - v = 3.5m/s: class D

### Water repellency version "+ options":

  - v = 0.0m/s: class A

  - v = 0.5m/s: class B

  - v = 1.0m/s: class B

  - v = 1,5m/s: class C

  - v = 2.0m/s: class C

  - v = 2.5m/s: class D

  - v = 3.0m/s: class d

  - v = 3.5m/s: class D

### Attenuation value

  - Rw (C;Ctr) (in dB): 17 (-1;-3)

## Complies with or tested in accordance with the following standards:

- Qualicoat Seaside type A (if painted finish)

- Qualanod (if anodised finish)

- EN 573 - EN AW-6063 T66 and EN AW-6060 T66: aluminium alloy & hardening

- EN 13030: water resistance and determination of Ceand Cdcoefficients

- EN 1990, EN 1991, EN 1999: strength calculations

- EN ISO 10140: acoustic measurements